## Management Planning Checklist
Management Planning Checklist
System Name: |  |  | Date:
Management Name(s):
# | Management Output | Supporting Documents | Person Responsible | Not Started ✓ | In Progress ✓ | Complete ✓
1 | System Information | System Design Documents Checklist (new installation) or System Assessment (taking over) |  | ❑ | ❑ | ❑
2 | Service Agreements & Contracts | Service Agreements & Contracts Checklist |  | ❑ | ❑ | ❑
3 | Roles & Responsibilities | Roles & Responsibilities Outline Operator Competency Checklist Operator Tools & Supplies Checklist Technician Tools & Supplies Checklist |  | ❑ | ❑ | ❑
4 | Safety Responsibilities | Safety Responsibilties Checklist |  | ❑ | ❑ | ❑
5 | Data Management Plan | Data Management Responsibilities Daily O&M Checklist Daily Water Production Form Daily Maintenance Form Weekly Maintenance Checklist Quarterly Maintenance Checklist Annual Maintenance Checklist |  | ❑ | ❑ | ❑
6 | Asset Management Plan | Parts Suppliers & Warranties List Weekly Tools & Supplies Inventory Form |  | ❑ | ❑ | ❑
7 | Financial Sustainability Plan | Financial Sustainability Worksheet |  | ❑ | ❑ | ❑

## System Documentation - New
New System Documentation Checklist
System Name:
Management Name(s):
Date:
The following information should be received as part of the handover process for a new SPWS. This documentation provides a clear record of the component parts and the manufacturer's maintenance and repair guidelines.
# | System Document | ✓
1 | System Assessment Report | ❑
2 | Design Documentation | ❑
3 | Project Layout | ❑
4 | As-built Drawings | ❑
5 | Project Budget | ❑
6 | Parts Suppliers & Warranty Information | ❑
7 | Technical Specifications for Major Components, such as:
| Solar Panels | ❑
| Pump | ❑
| Pump Controller (or Solar Inverter, if applicable) | ❑
| Electrical Controls & Protections | ❑
| Water Treatment Equipment | ❑
| Remote Monitoring Equipment | ❑

## System Assessment - Take Over
System Take Over Assessment
System Name:
Management Name(s):
Date:
# | Item | Data
A. Location, Participants, & Summary
Location Information
A1 | System name:
A2 | Village/Town:
A3 | District:
A4 | Region:
A5 | Country:
A5 | GPS Coordinates:
Inspection Participant Details
A6 | Inspection date:
A7 | Inspector:
A8 | Designer:
A9 | Contractor:
A10 | Handover entity:
A11 | Participants:
Executive Summary
A12 | System approved for immediate operation? | ❑ Yes ❑ No
A13 | Recommendations:
A14 | Date of submission:
# | Item |  | Inspection/Commissioning Data
B. System Parameters & Components Information
Solar Array
B1 | GPS Coordinates of solar array:
B2 | Number of panels (total):
B3 | Manufacturer of solar panels:
B4 | Rated power of solar panels (in W, per panel):
B5 | Number of panels (in series):
B6 | Do ALL PANELS in each series have exactly the same rating? |  | ❑ Yes ❑ No
B7 | Number of series groups (strings in parallel):
B8 | Total wattage output (STC):
B9 | Total voltage output (STC):
B10 | Spare solar panel information (if available):
B11 | Source circuit (before combiner box) wire size:
B12 | Source circuit wire type:
B13 | Output circuit (after combiner box) wire size:
B14 | Output circuit wire type:
Well
B15 | GPS Coordinates of well:
B16 | Well depth:
B17 | Casing diameter:
B18 | Static water level:
B19 | Dynamic water level:
B20 | Yield test results (conduct a yield test if more than 1 year since last test):
B21 | Water quality test (obtain water from source and label for testing): |  | ❑ Complete
Pump (remove from well to inspect)
B22 | Pump manufacturer:
B23 | Pump model & serial number:
B24 | Pump capacity (rated flow and pressure):
B25 | Is a warranty available? |  | ❑ Yes ❑ No
B26 | Depth of pump installation:
B27 | Pumping installer (if different than contractor named above):
B28 | Is the pump free of damage, dents, dirt, debris, etc? |  | ❑ Yes ❑ No
B29 | Is the the safety cable/rope in good condition? |  | ❑ Yes ❑ No
B30 | Does the underwater cable splice have mechanical/electrical integrity? |  | ❑ Yes ❑ No
B31 | Is the low water sensor unobstructed? |  | ❑ Yes ❑ No
B32 | Are all pipe joint sealed and secure? |  | ❑ Yes ❑ No
B33 | Is the connect of the water pipe to the wellhead secure? |  | ❑ Yes ❑ No
B34 | Is there proper strain relief for the submersible cable at the wellhead? |  | ❑ Yes ❑ No
B35 | Is the well cap securely bolted in place? |  | ❑ Yes ❑ No
B36 | Is there a pressure gauge installed at the pump?
B37 | Take a picture of the wellhead enclosure. |  | ❑ Complete
Electrical House | Charge Controller/Motor-Pump Controller
B38 | GPS Coordinates of electrical house:
B39 | Pump controller manufacturer:
B40 | Pump controller model & serial number:
B41 | Pump controller current (amperage) Rating:
B42 | Is an operations manual for the pump controller available on site? | Yes/No | ❑ Yes ❑ No
B43 | Solar inverter manufacturer (if aoolicable):
B44 | Solar inverter model & serial number (if applicable):
B45 | Solar inverter current (amperage) rating (if applicable):
B46 | Solar inverter efficiency (if applicable):
B47 | Is an operations manual for the pump solar inverter available on site? | Yes/No | ❑ Yes ❑ No
Pressure Line | Pressure Line
B48 | Size and type of pressure line (well to water tank):
B49 | Length of pressure line from well to water tank):
B50 | Total head (elevation change) from ground level at well to water tank inlet:
Water Storage Tank | Water Storage
B51 | GPS Coordinates of water tank:
B52 | Material of tank tower: |  | ❑ Brick ❑ Metal ❑ Other: __________________
B53 | Material of water tank:
B54 | Size of water tank:
B55 | Is the overflow screened? |  | ❑ Yes ❑ No
B56 | Is a float valve (or other tank-full control) installed? |  | ❑ Yes ❑ No
B57 | Is there a tank drain separate from the distribution pipe? |  | ❑ Yes ❑ No
Water Distribution & Community Access Points | Water Mainline
B58 | Material of distribution pipe:
B59 | Size (diameter) of distribution pipe:
B60 | Number of distribution lines:
B61 | Number of gate valves installed
B62 | Number of tap stands (if applicable):
B63 | Number of building connections (if applicable):
B64 | Number and type of any other community access points installed:
B65 | Are the community access points in proper working condition? | Cleared / Not cleared | ❑ Yes ❑ No
Operations & Maintenance | Operation and Maintenance
B66 | Was Operations & Maintenance training conducted? | Yes/No | ❑ Yes ❑ No
B67 | If yes, list the participants:
B68 | Operating entity (if applicable):
B69 | Tools available (if any):
B70 | Warranties & Contractor (if any):
B71 | Repairs conducted (if any):
# | Component | Activity | Results
C. Operating Performance (Functionality Tests)
C1 | Borehole yield | Conduct a yield test on the well if not done in the past year.
C2 | Dry run sensor | Test the dry run sensor (low water probe) to ensure it is functioning.
C3 | Water quality | Obtain a water sample from the water source and after treatment (if applicable) for testing. | Attach water quality report
C4 | Solar array | Check that all connections are secure.
C5 |  | Measure the output .
C6 | Pump | Check pump power consumption and record in power consumption for m3 pumped.
C7 |  | Measure pump capacity in liters per minute (LPM) against expected.
C8 | Pump controller (or solar inverter) | Check operation of pump controller (and Solar Inverter, if applicable).
C9 |  | Measure input power.
C10 |  | Measure output power.
C11 | Piping and water treatment equipment | Check valve functionality. If valves are found to be tight they may need to be lubricated. If they are found to be stuck they may need to be replaced.
C12 | Float switch | Check function of the tank float switch
C13 | Community access points' | Measure the flow rate at each community access point. | Point 1: Point 2: Point 3: Point 4: Point 5:
C14 | System pressure | Check pressure in EPAnet or similar software to ensure correct pipe sizing.
# | Item | Result | Notes
D. Community Socio-Economic Assessment
General Community Information
D1 | Catchment area (Check all that are present in the system's service area.) | ❑ Villages ❑ Households ❑ Schools ❑ Businesses ❑ Religious Centers ❑ Markets
D2 | Total population:
Socio-Economic Information
Interview a random selection of water users
D3 | Are users willing to pay? | ❑ Yes ❑ No
D4 | Are users able to pay? | ❑ Yes ❑ No
D5 | Average monthly HH income:
D6 | Current water fee (if any, record per HH/jerry can/m3):
Water Distribution System | Distribution
D7 | Total number of community access points:
D8 | Number of tap stands:
D9 | Number of yard taps:
D10 | Number of building connections:
D11 | Community Access Point Details (Copy/record this information for all community access points. Include all types of community access points, such as tap stands, yard taps, HH connections, and institutions.) | Type of connection:
D12 |  | GPS Coordinates:
D13 |  | Number of taps:
D14 |  | Number of HHs served:
D15 |  | Hours operational:
D16 |  | Queue time (if any):
D17 |  | Flow rate:
D18 |  | Metered? ❑ Yes ❑ No
Water Demand (Daily) | Demand
D19 | Demand at tap stands: |  | Total # HHs using tap stands * 6 * 20 L/day
D20 | Demand at yard taps: |  | Total # HHs using yard taps * 6 * 50 L/day
D21 | Demand at HH connections: |  | Total # HHs using building connections * 6 * 100 L/day
D22 | Demand from institutions:
D23 | Schools |  | Day students * 5 L/day Boarders * 50 L/day
D24 | Health centers |  | Outpatients * 5 L/day Beds (inpatient capacity) * 50 L/day
D25 | Religious centers/Markets |  | Assess on case-by-case basis
D26 | Total daily water demand:

## Service Agreements Checklist
Service Agreements & Contracts Checklist
System Name:
Management Name(s):
Date:
# | Contract With | Contract Purpose | ✓ | Effective Date
|  |  |  | Start | End
1 | Product Suppliers | Warranty and defect liability arrangement, ideally for periods of two or more years (recommend a minimum requirement of one-year). *This is usually done at the time of equipment purchase and installation by the supplier. Check to make sure that this is the case and, if not, prepare the contract and contact the supplier. | ❑
2 | Service Providers | Overhaul and replacement of equipment arrangement. | ❑
3 | System Technician(s) | Service delivery arrangement should be established with key responsibilities. | ❑
4 | System Operator(s) | Service delivery arrangement should be established with key responsibilities. | ❑
5 | Water Users | A fee amount and schedule with transfer arrangements should be agreed on for covering ongoing costs through a combination of funds. | ❑

## Roles & Responsibilities Guide
Roles & Responsibilities Guide
System Name:
Management Name(s):
Technician Name(s):
Operator Name(s):
Date:
# | Primary Responsibility | Support
System Management
1 | Safety Protocols & Risk Prevention | System Operator System Technician
Create safety strategies to protect personel.
Provide safety equipment (personal protective equipment).
Provide in-depth safety training to all personel.
2 | O&M Workplan | System Technician
Establish O&M plan for the system.
Hire qualified personel.
Provide O&M plan to Operators and Technicians.
3 | Data Management | System Operator System Technician
Determine what system data to collect and provide forms.
Determine the data reporting procedures and frequency.
Maintain all sumbitted records.
4 | Management of Parts & Supplies | System Operator System Technician
Establish site security and theft prevention procedures.
Implement an inventory system for supplies and spare parts.
Maintain a stock of all routine supplies and spare parts.
Manage warranties, liabilities, and major repairs.
Procure major replacement components.
5 | Financial Management | Tap Operators (if applicable)
Establish water fees/tariffs based on life-cycle costing.
Establish water fee/tariff collection and deposit procedures.
Maintain system financial records.
Manage system budget for ongoing O&M and replacements.
System Operator
6 | Safety Protocols & Risk Prevention | System Management System Technician
Follow all safety protocols at all times.
Maintain site security at all times.
Report safety or security concerns.
7 | Routine Operation | System Management System Technician
Follow established pumping procedures (start up/shut down).
Maintain pumping schedule to ensure reliable water supply.
Perform water quality testing to ensure safe water.
8 | Preventative (minor) Maintenance | System Management System Technician
Maintain site cleanliness.
Perform weekly inspections (as detailed in O&M workplan).
Perform minor repairs (as detailed in O&M workplan).
9 | Data Recording | System Management
Complete data collection forms (as detailed in O&M workplan).
Submit forms to Management (as detailed in O&M workplan).
10 | Repair (major) Maintenance | System Technician
Assist Technician with quarterly/annual inspections.
Assist Technician with minor and major repairs.
System Technician
11 | Preventative (minor) Maintenance | System Operator System Management
Perform anuual maintenance (as detailed in O&M workplan).
Perform quarterly maintenance (as detailed in O&M workplan).
Perform minor repairs as needed.
12 | Repair (major) Maintenance | System Operator System Management
Perform major repairs and replacements as needed.
13 | Data Recording | System Management
Complete data collection forms (as detailed in O&M workplan).
Submit forms to Management (as detailed in O&M workplan).

## Safety Responsibility Checklist
Safety Responsibilities
System Name:
Managment Name(s):
Technician Name:
Operator Name:
Date:
# | Responsibility |  | Initial
1 | Safety is the resposibility of EVERYONE in the workplace. |  | x _______
2 | All workers have the right to: |  | x _______
Know about hazards.
Be provided with safety training and protective equipment.
Refuse unsafe work.
SYSTEM MANAGEMENT is responsible for:
3 | Establish safety protocols to protect personnel. |  | x _______
4 | Provide training to ensure Operators and Technicians can safely accomplish their roles. |  | x _______
5 | Provide and maintain safety and personal protective equipment (PPE). |  | x _______
6 | Respond to and taking corrective action on any reported safety concerns. |  | x _______
SYSTEM OPERATORS and TECHNICIANS are responsible for:
7 | Follow all safety protocols and precautions at all times. |  | x _______
8 | Properly use safety and personal protective equipment (PPE). |  | x _______
9 | Act professionally at all times. |  | x _______
10 | Identify and report safety hazards or potential safety concerns. |  | x _______
11 | Immediately report any injury or accident to Management. |  | x _______
In case of injury CALL: xx-xx-xx-xx
X ______________________________________________________________ |  | _________________
Signature |  | Date

## Operator Competency Check (Gen)
Operator Competency Checklist (General)
System Name:
Management Name(s):
Technician Name:
Operator Name:
Date:
To safely operate and maintain small drinking water systems, a System Operator must have the following competencies (knowledge, skills, and attitude).
* See Operator Competency Checklist (System Operations) for an on-the-job competency check to evaluate Operators.
# | Competency | ✓
1 | Demonstrate safety protocols during all operations and maintenance procedures. | ❑
2 | Perform common maintenance and routine checks of electrical or fuel-powered water supply systems. | ❑
3 | Perform common maintenance and routine checks of water treatment systems. | ❑
4 | Perform common maintenance and routine checks of storage, distribution, and water collection points, whether at the household level or at kiosks. | ❑
5 | Troubleshoot issues and perform minor repairs of system components. | ❑
6 | Perform corrective actions to resolve identified issues related to water quantity and distribution. | ❑
7 | Collect and test water samples (residual/free chlorine, turbidity). | ❑
8 | Interpret water quality testing results and perform corrective actions to resolve issues. | ❑
9 | Accurately complete, manage, and submit data records and monitoring forms. | ❑
10 | Communicate effectively with community members about water availability and acceptability. | ❑
11 | Communicate effectively with community members about locally available household water treatment options in case of an absent or failing water treatment system. | ❑
12 | Assist in system design processes to ensure system meets community needs. | ❑
13 | Communicate effectively to the System Technician for issues as required. | ❑
14 | Support and supervise Assistant Operators. | ❑

## O&M Tasks Overview
O&M Tasks Overview
System Name:
Managment Name(s):
Technician Name:
Operator Name:
Date:
# | Responsibility | Primary Responsibility | Supporting Responsibility
DAILY
| Routine operation of water system. | Operator | Management Technician
| Maintain site security and cleanliness. | Operator | Management
| Visually inspect solar panels and electrical boxes. | Operator | Technician
| Check residual chlorine (and turbidity, if applicable). | Operator | Technician
| Complete Daily Water Production Form and Daily Maintenance Form. | Operator | Management
WEEKLY
| Check for modifications or animal activity. | Operator | Management
| Perform visual inspections and minor maintenance: | Operator | Technician Management
Solar array (wash solar panels), electrical house, wiring and grounding, wellhead, water treatment house, water tank, piping (pressure and distribution), community access points
| Complete Weekly Maintenance Checklist and Weekly Tools & Supplies Inventory Form. | Operator | Management
QUARTERLY
| Perform visual inspections and major maintenance: | Technician | Operator Management
Electrical house and all electrical equipment
| Confirm functionality of equipment: | Technician | Operator
Float Switch, remote monitoring system, sensors (as applicable), water quality testing equipment
| Observe Operator performing water quality tests. | Technician | Operator
| Test water quality: | Technician | Operator
Residual chlorine, turbidity, bacteria
| Complete Quarterly Maintenance Checklist. | Technician | Management Operator
ANNUAL
| Perform full inspections and major maintenance: | Technician | Operator Management
Structures, fencing/gates, lights, electrical equipment and protections, wiring connections, borehole, pump, water treatment equipment, piping, valves, water meter, remote monitoring system, generator (if applicable)
| Perform a continuity test. | Technician | Operator Management
*Every 3-5 years or as required by local regulations
| Perform a ground resistance test. | Technician | Operator Management
*Every 3-5 years or as required by local regulations
| Observe Operator performing pumping procedures. | Technician | Operator
| Perform a yield test. | Technician | Operator Management
| Collect water samples for full water quality analysis. | Technician | Operator Management
| Complete Annual Maintenance Checklist. | Technician | Management Operator

## Data Management
Data Management Plan
System Name:
Management Name(s):
Technician Name:
Operator Name:
Date:
# | Data to Record | Frequency of Data | Form to Use | Submission to Management
OPERATORS are responsible for recording and submitting the following data:
1 | Water Meter Reading | Start and end of all pumping cycles | Daily Water Production Form | Weekly
2 | Total Daily Water Production | Daily
3 | Residual Chlorine | Daily
4 | Turbidity (if applicable) | Daily
5 | Weather Conditions (sunny, cloudy, rainy) | Daily | Daily Maintenance Form | Weekly
6 | Pumping Pressure | Daily (specifiy set times)
7 | Power (from pump controller) | Daily (specify set times, noon recommended)
8 | Alarms (from pump controller) | Daily (as present)
9 | Maintenance Completed | Daily (as appliable)
10 | Community Feedback | Daily
11 | Completion of Weekly Maintenance Tasks | Weekly | Weekly Maintenance Checklist | Weekly
12 | Areas of Concern or Future Repairs | Weekly
13 | Inventory | Weekly | Weekly Tools & Supplies Form | Weekly
TECHNICIANS are responsible for recording and submitting the following data:
14 | Completion of Quarterly Maintenance Tasks | Quarterly | Quarterly Maintenance Checklist | Quarterly
15 | Areas of Concern or Future Repairs | Quarterly
16 | Follow Up to be Completed by Operator | Quarterly
17 | Completion of Annual Maintenance Tasks | Annually | Annual Maintenance Checklist | Annually
18 | Borehole Yield Test | Annually | Provided by Technician or Hydrogeologist | Annually
19 | Full Water Quality Analysis | Annually | Provided by Water Quality Lab | Annually

## Parts Contacts Warranties
Parts Suppliers & Warranties - Major Components
System Name: Newa Community
Management Name(s):
Date:
Type of Equipment | Part Number or Name | Manufacturer | Specifications # | Supplier Contact # | Warranty* | Expected Lifespan
Solar Panels | SPR-P5-525-UPP | Sunpower | 1 |  | 10-year product 25-year performance | 25 years
Pump | 11 SQF-2 | Grundfos | 2 |  | 2-year product | 7 years
Pump Controller | CU200 | Grundfos | 3 |  | 2-year product | 10 years
3-Way Disconnect Switch | 32 A Onload Changeover Switch | Havells |  |  | 2-year product | 10 years
DC Combiner Box | IP65-rated electrical enclosure | Misc. |  |  | N/A | 10 years
| 20 kA, 600 VDC Surge Protection | Misc. |  |  | N/A | 3 years
| 15 A, 600 VDC Circuit Breaker | Misc. |  |  | N/A | 3 years
| 15 A Fuses | Misc. |  |  | N/A | 3 years
AC Protections Box | AVS30 (voltage protection) | Sollatek | 4 |  | 1-year product | 3 years
| 20-A, 240 V Overcurrent protection | Misc. |  |  | N/A | 3 years
| 20 kA, 240/480 V Surge Protection | Misc. |  |  | N/A | 3 years
Water Treatment | Erosion Chlorinator | Water Mission | 5 |  |  | 15 years
Remote Monitoring | SatWater Communicator V3 | Water Mission | 6 |  |  | 10 years