## TECH Tools & Supplies List
Technician Tools & Supplies Checklist
System Name:
Technician Name:
Operator Name:
Date:
Item # | Quantity | Item | Purpose | ✓
Quarterly Tasks
1 | 1 pair | Foot protection (protective shoes) | Personal protective equipment | ❑
2 | 1 | Hard hat | Personal protective equipment | ❑
3 | 1 | Eye Protection | Personal protective equipment | ❑
4 | 1 | Respiratory protection | Personal protective equipment | ❑
5 | 1 pair | Gloves | Personal protective equipment | ❑
7 | 1 | Writing utensil (pen/pencil) | Data recording | ❑
8 | 1 | Quarterly Maintenance Form | Data recording | ❑
9 | 1 | Toolbag | To hold all tools and supplies | ❑
10 | 1 | Ladder | Inspecting solar array and structures | ❑
11 | 1 set | Adjustable wrenches | Tightening bolts, as needed | ❑
12 | 1 set | Insulated screwdriver set | Opening electrical boxes, tighten wires | ❑
13 | 1 | Chlorine Test Kit with Reagents | Testing residual chlorine | ❑
14 | 1 | Turbidity Test Kit (if needed) | Testing turbidity | ❑
15 | 1 | Bacteria Test Kit (or sample bags) | Testing total and fecal coliforms | ❑
Annual Tasks (the following are needed in addition to the above for annual mainenance tasks)
16 | 1 | Annual Maintenance Form | Data recording | ❑
17 | 1 | Multimeter *Voltage greater than system, 1000 V is best. | Checking electrical measurements | ❑
18 | 1 | Irradiance meter, if applicable | Checking irradiation sensor | ❑
19 | 1 | Piezometer or water level sensor | Measuring water table | ❑
20 | 1 | Tape measure | Measuring water table or equipment | ❑
21 | 1 | Borehole camera *highly reccomended | Inspecting borehole and casing | ❑

## Quarterly Maintenance Checklist
Quarterly Maintenance Checklist
System Name:
Technician Name:
Operator Name:
Date:
Prepare for the Site Visit
1 | Call the System Operator:
a) Inform them of the date of the visit
b) Ask if there are any current concerns that need to be addressed
c) Ask if there are any supplies that need to be restocked
2 | Review the design specifications to remind yourself of the system components (ex. Pump type/size, chlorination system etc.) and the current point in the life cycle of the parts.
3 | Review the reporting forms collected throughout the year by the Operator and analyze to determine if there are any issues impacting expected system performance.
a) If the data indicates a decline or malfunction in water supply or quality, be ready to perform all annual maintenance activities and to identify the cause of the decline.
b) If the data shows that the water supply and quality is trending as expected, perform all annual maintenance activities so the system will continue to supply water consistently.
4 | Prepare all tools, materials and consumables required for any maintenance tasks, water quality testing, and restocking the inventory as needed.
Maintenance Task |  | ✓ | Notes
A. Electrical House
A1 | Check for structural damage. | ❑
A2 | Check for damaged pipes entering or exiting. | ❑
A3 | Check for erosion around the foundation. | ❑
A4 | Check for leaks in the roof and walls. | ❑
A5 | Check for rotting wood. | ❑
A6 | Check for and remove waste and debris. | ❑
A7 | Check for and remove cobwebs or insect nests. | ❑
A8 | Check the door lock. Replace if needed. | ❑
B. Electrical Equipment
B1 | Check inside all electrical boxes for corrosion, insects, dust, smoke/burns, or water intrusion. | ❑
B2 | Check that all wires are firmly connected (isolate each electrical box first). | ❑
B3 | Clean the vents and screens on all electrical boxes. | ❑
B4 | Check that all electrical equipment is properly and securely mounted to the wall/supports. | ❑
B5 | Check that display screens are clean and remove any dust or cobwebs. | ❑
B6 | Check the seals around enclosure covers and wire entrances to ensure they are tight. | ❑
B7 | Check that the float switch is functioning. | ❑
B8 | Inspect protective equipment (e.g., dry run sensor), as needed. | ❑
B9 | Check that the remote monitoring system is functioning. | ❑
C. Water Treatment House
C1 | Check that chlorine is stored safely. | ❑
C2 | Check that water quality testing equipment is functioning. | ❑
C3 | Observe the Operator performing water quality tests to confirm proper procedure. | ❑
C4 | Test the residual chlorine at the closest and farthest community access point. | ❑ | Chlorine (ppm)
C5 | Test the turbidity at the closest and farthest community access point. | ❑ | Turbidity (NTU)
C6 | Test for bacteria (total and fecal coliforms) at the closest and farthest community access point (or collect samples to be sent to off-site water quality lab). | ❑ | Total Coliforms (CFU/100 mL)
Fecal Coliforms (CFU/100 mL)
Additional Comments
Follow Up Items for Operator
x _______________________________________ |  |  | _________________
Technician Signature |  |  | Date
x _______________________________________ |  |  | _________________
Operator Signature |  |  | Date
SUBMIT TO SYSTEM MANAGEMENT

## Annual Maintenance Checklist
Annual Maintenance Checklist
System Name:
Technician Name:
Operator Name:
Date:
Prepare for the Site Visit
1 | Call the System Operator:
a) Inform them of the date of the visit
b) Ask if there are any current concerns that need to be addressed
c) Ask if there are any supplies that need to be restocked
2 | Review the design specifications to remind yourself of the system components (ex. Pump type/size, chlorination system etc.) and point in the life cycle of the parts.
3 | Review the reporting forms collected throughout the year by the Operator and analyze to determine if there are any issues impacting expected system performance.
a) If the data indicates a decline or malfunction in water supply or quality, be ready to perform all annual maintenance activities and to identify the cause of the decline.
b) If the data shows that the water supply and quality is trending as expected, perform all annual maintenance activities so the system will continue to supply water consistently.
4 | Prepare all tools, materials and consumables required for any maintenance tasks, water quality testing, and restocking the inventory as needed.
Maintenance Task |  | ✓ | Notes
A. Structural Inspections
A1 | Check the condition of fences, gates, and locks for security. | ❑
A2 | Check all walls, floors, and roofing for cracks, damage, rust, and animal activity/nests. | ❑
A3 | Check the area around the wellhead for damages, leaks, and animal activity/nests. | ❑
A4 | Check that water treatment chemicals are properly stored. | ❑
A5 | Check the condition of all lights and electrical sockets. | ❑
A6 | Check the condition of the water storage tank and structure. | ❑
A7 | Check the taps at community access points. | ❑
A8 | Check for and remove waste and debris. | ❑
B. Solar Array
B1 | Check the solar panels for dust or debris. | ❑
B2 | Check all clamps and bolts to ensure the solar panels are securely mounted. | ❑
B3 | Check the solar structure for cracks or rust. | ❑
B4 | Check that all wiring connections are secure. | ❑
B5 | Check the electrical measurements of the solar panels to ensure functionality. | ❑
B6 | Check the functionality of the irradiation sensor, if applicable. | ❑
C. Grounding and Bonding
C1 | Check for corrosion, damage, or loose connections in grounding wires. | ❑
C2 | Check that connections at the grounding rod(s) are tight and secure. | ❑
C3 | Check for and remove debris and dust in the earthing chamber, if applicable. | ❑
C4 | Perform a continuity test. *Every 3-5 years or as required by local regulations | ❑
C5 | Perform a ground resistance test. *Every 3-5 years or as required by local regulations | ❑
D. Electrical Equipment
D1 | Check for dust or dirt on all electrical equipment. | ❑
D2 | Check for proper seals around wire entrances and conduit. | ❑
D3 | Check that all electrical covers properly close and seal. | ❑
D4 | Check that all electrical equipment and wiring is properly labelled and identified. | ❑
D5 | Tighten cables and wire connections. | ❑
D6 | Check that all electrical equipment is functioning properly. | ❑
D7 | Check that all electrical protections (fuses and surge) are functioning properly. | ❑
D8 | Complete a measurement inspection (current, voltage, resistance, power). | ❑
D9 | Complete a thermography inspection. | ❑
D10 | Observe the Operator performing start up, shutdown, and change over procedures. | ❑
E. Generator (if applicable)
E1 | Check the exhaust system for damage or blockages. | ❑
E2 | Check all electrical connections are secure and free of corrosion. | ❑
E3 | Check engine oil and filter, as needed. | ❑
E4 | Change fuel filter, as needed. | ❑
E5 | Checks for leaks in the coolant system. Inspect and replace coolant, as needed. | ❑
E6 | Inspect and replace air filters, as needed. | ❑
E7 | Check the radiator for blockages or dirt. Clean as needed. | ❑
E8 | Conduct a load test to ensure the generator is operating properly. | ❑
E9 | Ensure all safety features and alarms are functioning properly. | ❑
E10 | Check the condition of the battery and clean terminals, as needed. | ❑
F. Remote Monitoring
F1 | Review all data logs for potential issues with the remote monitoring system or sensors. | ❑
F2 | Test the sensors to confirm functionality, as needed. | ❑
G. Well & Pump
G1 | Check the water table levels (static water level). | ❑
G2 | Examine the borehole casing for corrosion, damages, or leaks. | ❑
G3 | Ensure the borehole structure is stable without concern of collapse. | ❑
G4 | Examine the wellhead for leaks or damage, including the well seal and discharge pipes. | ❑
G5 | Check around the wellhead for waste or debris. | ❑
G6 | Perform a yield test to check the flow rate and performance of the borehole. | ❑
G7 | Compare the test results with the borehole's original yield test results. | ❑
H. Pump Maintenance
H1 | Review the yield test data and Operator logs for any potential performance issues. | ❑
H2 | If there are indiciations of pump decline, test the voltage, current, resistance, and power. | ❑
H3 | If the electrical tests indicate an issue, remove the pump for cleaning, inspect for damage, and evaluate if the pump needs to be replaced. | ❑
I. Water Meter
I1 | Check the piping connections around the water meter. | ❑
I2 | Test the water meter to ensure it is reading accurately. | ❑
J. Water Treatment House
J1 | Check that all chemicals are properly stored in the water treatment house. | ❑
J2 | Check the valves of the treatment system for damage, leaks, and functionality. | ❑
J3 | Collect water samples to perform all biological, chemical, and physical water quality tests. | ❑
K. Water Storage and Distribution
K1 | Check the length of the pipe system for leaks, damage, or exposed pipes. | ❑
K2 | Ask the Operator to show you any areas where the pipe has been reburied. | ❑
K3 | Check that all pipe connections and fittings are securely tightened. | ❑
K4 | Check that all valves are operating correctly.
K5 | Check the storage tank for signs of contamination. | ❑
K6 | Check that the float switch is operating correctly. | ❑
Additional Comments
Follow Up Items for Operator
x _______________________________________ |  |  | _________________
Technician Signature |  |  | Date
x _______________________________________ |  |  | _________________
Operator Signature |  |  | Date
SUBMIT TO SYSTEM MANAGEMENT

## Operator Competency Assessment
Operator Competency Assessment
System Name:
Technician Name:
Operator Name:
Date:
This question/answer checklist is to be used by the Technician to train and evaluate the Operator. While Operator training may cover even more topics, these are the key competencies that the Operator must be able to demonstrate to effectively start up, operate, and shut down the water system. The Operator should correctly answer and demonstrate these competencies.
* See Operator Competency Checklist (General) for all job competencies related to the Operator role.
# | Competency | Pass | Fail | N/A
1 | What do you do before starting the solar-powered water system? Answer: Make sure all valves are in the proper position (includes at the wellhead, pipeline, water treatment, and water storage tank). | ❑ | ❑ | ❑
2 | How do you start the solar powered water system? Answer: Turn the Disconnect Switch to "On/Solar/DC" and turn the pump on using the button on the pump controller. Never plug/unplug wires. | ❑ | ❑ | ❑
3 | How do you shut the solar-powered water system down? Answer: Turn off the pump using the button on the pump controller and turn the Disconnect Switch to "Off". Drain the chlorinator. Never plug/unplug wires. | ❑ | ❑ | ❑
4 | How do you switch to generator (AC) power? Answer: Turn the pump off using the button on the pump controller and turn the Disconnect Switch to "Off". Turn the generator on and wait two minutes. Turn the Disconnect Switch to "On/Generator/AC" and turn the pump on using the button on the pump controller. | ❑ | ❑ | ❑
5 | How often should you check the solar panels for dust and dirt? Answer: Every day. | ❑ | ❑ | ❑
6 | How often should you wash the solar panels? Answer: At least once per week, but as often as needed to keep them clear of dust and dirt. | ❑ | ❑ | ❑
7 | Why is it important to keep the solar panels clean? Answer: Dust and dirt on the solar panels will reduce the amount of power, which means less water will be produced. Even the smallest amount of dust (or shading from vegetation) can have a significant impact on water production. | ❑ | ❑ | ❑
8 | How do you test the chlorine? Answer: Use the Chlorine Test Kit (or chlorine test strips) to measure the residual chlorine. | ❑ | ❑ | ❑
9 | What should the residual chlorine be coming out of the tap? Answer: The residual chlorine should be 0.2-0.5 ppm at the community access points under normal conditions. | ❑ | ❑ | ❑
10 | What should the residual chlorine be exiting the water treatment system? Answer: The residual chlorine should be 0.5-0.8 ppm at the water treatment system under normal conditions. (If the water distribution network is large, it may need to be higher, such as 1.2-2.0 ppm). | ❑ | ❑ | ❑
11 | What do you do if the water at the tap does not have least 0.2 ppm? Answer: Adjust the amount of chlorine during water production. | ❑ | ❑ | ❑
12 | How do you increase or decrease the chlorine level? Answer: Turn the chlorine control valves on the chlorinator (clockwise to increase counter-clockwise to decrease). | ❑ | ❑ | ❑
13 | Why is having the proper chlorine level important? Answer: Low chlorine levels increase the risk of microbial contamination, making the water unsafe to drink. High chlorine levels cause a strong smell and taste. Significantly high levels of chlorine can be unsafe. | ❑ | ❑ | ❑
14 | What should you do with the chlorinator every time you shut down the solar powered water system? Answer: Drain the chlorinator. | ❑ | ❑ | ❑
15 | Why is draining the chlorinator important? Answer: Draining the chlorinator prevent over-chlorination and the build up of chlorine fumes inside the chlorinator. | ❑ | ❑ | ❑
16 | How do you drain that chlorinator? Answer: After the pump has been turned off and water has stopped flowing through the chlorinator, open the drain valve. | ❑ | ❑ | ❑
17 | How do you complete the Daily Water Production form? Answer: Record the water meter reading at the start and end of each pumping session, the residual chlorine at the closest and furthest community access point, and the total water produced (at the end of the day). | ❑ | ❑ | ❑
18 | How do you take a water meter reading? Answer: Read the dial on the face of the water meter. Record the number and the units. | ❑ | ❑ | ❑
19 | How do you complete the Daily Maintenance form? Answer: Record the weather conditions, pumping pressure, power, alarms (if present), and any key notes, observations, or activities performed. | ❑ | ❑ | ❑
20 | How do you take a power reading? Answer: The power is displayed digitally on the pump controller. Record the number and units. | ❑ | ❑ | ❑
21 | How do you know if there are any alarms? Answer: Alarms are displayed on the pump controller as red LED lights. | ❑ | ❑ | ❑
22 | What are the most common pump alarms you might encounter? Answer: The most common alarms are WELL DRY, TANK FULL, and FAULT. | ❑ | ❑ | ❑
23 | What do you do if the water system stops working or there is a problem? Answer: Shut down the system and contact the System Technician and System Management. | ❑ | ❑ | ❑
x _______________________________________ |  | _________________
Technician Signature |  | Date
x _______________________________________ |  | _________________
Operator Signature |  | Date
SUBMIT TO SYSTEM MANAGEMENT